## Slide 1
College of Engineering
Oral Final Defense of Thesis entitled
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
BY
ROSIE MAY ANDES JAYVEE C. BUENAVENTURA
PRINCESS JANELLE M. CALIMUTAN
JHUDIEL F. CORDONATO
JONAS EISEN T. MANGUIAT
IAN MAR D. OCLARINO KRISTHEL M. OROZCO
JOHN LLOYD P. RAZON
BS Computer Engineering Candidate
ENGR. FLAVIANO L. URERA JR. (Adviser)
ENGR. CHONA MASACUPAN (Co-Adviser)
ENGR. NOIME G. ROBLES (Specialist)
ENGR. RAYMOND R. BALINO (Statistician)
ENGR. WILFREDO G. TUSO III (Panel Chair)
ENGR. LEONARDO A. VENANCIO (Panel Chair)

## Slide 2
OVERVIEW
  Introduction
  Objectives of the Study
  Research Paradigm/ Framework
  General Description and Features, Parts and Relevant Computations and Assumptions
  Special techniques and Procedure
  System Performance, Relevant Graphs and Figures, Analysis
  Findings, Conclusion and Recommendation
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON

## Slide 3
INTRODUCTION
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON

## Slide 4
OBJECTIVES
The general objective of this study is to develop and evaluate a real-time anomaly detection system for hybrid power operation using rule-based signal analysis.
This study specifically aims to:
Develop a monitoring and alert feature system that presents detected anomalies and notifies users during abnormal voltage conditions.
Design a rule-based mechanism for the real-time detection and classification of voltage anomalies, specifically spike, drift, and dropout.
Evaluate the performance of the developed system in terms of:
3.1 Accuracy
3.2 Precision
3.3 Recall
3.4 F1-Score
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON

## Slide 5
RESEARCH PARADIGM/ FRAMEWORK
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON

## Slide 6
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 2: Block Diagram of the System

## Slide 7
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 3. Overall Flow of the Anomaly Detection System

## Slide 8
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 3.1. Dropout Detection Flowchart for AC Grid Power Source

## Slide 9
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 3.2. Spike Detection Flowchart

## Slide 10
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 3.3. Drift Detection Flowchart

## Slide 11
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
Figure 4. Hardware Setup for Low-Voltage Pre-Testing

## Slide 12
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
Figure 5. Conceptual design of the real-time hybrid power voltage anomaly detection system

## Slide 13
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
Figure 6. Physical setup of the solar panel installation in the hybrid power system

## Slide 14
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 7. Schematic Diagram of the Proposed System
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
Figure 8. Pictorial Diagram of the Proposed System

## Slide 15
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
GENERAL DESCRIPTION AND FEATURES, PARTS AND RELEVANT COMPUTATIONS AND ASSUMPTIONS
Accuracy
Equation 1
Equation 2
Equation 3
Equation 4

## Slide 16
SPECIAL TECHNIQUES AND PROCEDURE
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
The study used rule-based signal analysis to detect and classify AC and DC voltage anomalies in a hybrid power system. Voltage readings were evaluated using predefined rules based on voltage magnitude, rate of change, and persistence over time to identify dropout, spike, drift, or normal conditions. A low-voltage pre-testing setup with a nominal voltage of 6.0 V was first used to safely validate and refine the detection logic before applying the calibrated rules to actual AC and DC sources. The system followed a detection sequence of dropout, spike, drift, then normal, and the results were recorded, displayed, and used for alert generation when needed.

## Slide 17
SPECIAL TECHNIQUES AND PROCEDURE
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 9. Interface of the kiosk

## Slide 18
SPECIAL TECHNIQUES AND PROCEDURE
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 10. User Interface Concept Architecture Design

## Slide 19
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Table 6. Percentage Distribution of Detected Voltage Conditions (No Load Phase: April 24–30)

## Slide 20
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 11. Distribution of Spike, Drift, and Dropout Anomalies During No-Load Operation
Graphical Presentation and Comparative Analysis of Detected Voltage Anomalies

## Slide 21
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Table 7. Percentage Distribution of Detected Voltage Conditions (With Load Phase: May 3–10)

## Slide 22
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Figure 12. Distribution of Spike, Drift, and Dropout Anomalies During With-Load Operation

## Slide 23
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Graphical Presentation and Comparative Analysis of Detected Voltage Anomalies
No-Load Phase
April 24, 2026
Figure 13. Grid and Inverter Voltage Trend (April 24)

## Slide 24
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Graphical Presentation and Comparative Analysis of Detected Voltage Anomalies
No-Load Phase
April 24, 2026
Figure 14. Solar PV and Battery Voltage Trend (April 24)

## Slide 25
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 25, 2026
Figure 15. Grid and Inverter Voltage Trend (April 25)

## Slide 26
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 25, 2026
Figure 16. Solar PV and Battery Voltage Trend (April 25)

## Slide 27
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 26,2026
Figure 17. Grid and Inverter Voltage Trend (April 26)

## Slide 28
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 26, 2026
Figure 18. Solar PV and Battery Voltage Trend (April 26)

## Slide 29
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 27, 2026
Figure 19. Grid and Inverter Voltage Trend (April 27)

## Slide 30
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 27, 2026
Figure 20. Solar PV and Battery Voltage Trend (April 27)

## Slide 31
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 28, 2026
Figure 21. Grid and Inverter Voltage Trend (April 28)

## Slide 32
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 28, 2026
Figure 22. Solar PV and Battery Voltage Trend (April 28)

## Slide 33
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 29, 2026
Figure 23. Grid and Inverter Voltage Trend (April 29)

## Slide 34
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 29, 2026
Figure 24. Solar PV and Battery Voltage Trend (April 29)

## Slide 35
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 30, 2026
Figure 25. Grid and Inverter Voltage Trend (April 30)

## Slide 36
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
April 30, 2026
Figure 26. Solar PV and Battery Voltage Trend (April 30)

## Slide 37
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
With Load Phase
May 3, 2026
Figure 27. Grid and Inverter Voltage Trend (May 3)

## Slide 38
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 3, 2026
Figure 28. Solar PV and Battery Voltage Trend (May 3)

## Slide 39
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 4, 2026
Figure 29. Grid and Inverter Voltage Trend (May 4)

## Slide 40
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 4, 2026
Figure 30. Solar PV and Battery Voltage Trend (May 4)

## Slide 41
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 6, 2026
Figure 31. Grid and Inverter Voltage Trend (May 6)

## Slide 42
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 6, 2026
Figure 32. Solar PV and Battery Voltage Trend (May 6)

## Slide 43
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 7, 2026
Figure 33. Grid and Inverter Voltage Trend (May 7)

## Slide 44
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 7, 2026
Figure 34. Solar PV and Battery Voltage Trend (May 7)

## Slide 45
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 8, 2026
Figure 35. Grid and Inverter Voltage Trend (May 8)

## Slide 46
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 8, 2026
Figure 36. Solar PV and Battery Voltage Trend (May 8)

## Slide 47
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 9, 2026
Figure 37. Solar PV and Battery Voltage Trend (May 9)

## Slide 48
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 9, 2026
Figure 38. Solar PV and Battery Voltage Trend (May 9)

## Slide 49
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 10, 2026
Figure 39. Grid and Inverter Voltage Trend (May 10)

## Slide 50
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
May 10, 2026
Figure 40. Solar PV and Battery Voltage Trend (May 10)

## Slide 51
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Table 8. Anomaly Type Distribution — Both Periods Combined.

## Slide 52
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Table 9. Classification Dataset Summary per Source and Period (Threshold-Verified)

## Slide 53
SYSTEM PERFORMANCE, RELEVANT GRAPHS AND FIGURES, ANALYSIS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
Table 10. System Performance Metrics per Period (Threshold-Verified Ground Truth)

## Slide 54
FINDINGS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
The study successfully developed and deployed a real-time anomaly detection system for hybrid power operation that monitored AC and DC voltage across four sources — utility grid, inverter AC output, solar photovoltaic panels, and battery storage. Controlled prototype testing confirmed the system correctly identified all simulated voltage conditions before field deployment. Over a 14-day monitoring period split into no-load (April 24–30) and with-load (May 3–10) phases, the system logged over 400,000 readings and classified 30,611 anomaly events, with dropout anomalies being the most dominant at 83.93% of all detected events. The solar PV source was the most consistently affected, primarily due to declining irradiance in the late afternoon and evening. Notably, the with-load phase showed improved overall stability at 92.98% normal readings compared to 89.99% during no-load, and the system achieved an overall accuracy of 97.71% and an F1-score of 91.15%.

## Slide 55
CONCLUSIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
The system effectively fulfilled its core objectives, delivering continuous voltage monitoring, rule-based anomaly classification, real-time visualization, and automated alerts throughout actual field deployment. The rule-based approach using voltage magnitude, rate of change, and persistence-based evaluation proved to be a functionally sound and interpretable method for distinguishing between normal and abnormal voltage conditions. The behavioral patterns observed across both phases confirmed that solar PV dropouts and utility grid undervoltage were the most recurring disturbances, while the hybrid inverter consistently maintained stable output. The presence of a connected load actually helped stabilize voltage behavior in the battery and inverter subsystems, and the system's stronger performance during the with-load phase further validated the reliability of the detection logic under real operating conditions.

## Slide 56
RECOMMENDATIONS
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON
The study recommends that the spike detection logic for the Inverter and Solar PV sources be reviewed and corrected to strictly enforce the defined percentage-based ΔV thresholds 5% and 10% of nominal voltage respectively to eliminate false positive detections, and that the drift detection rule for the Grid source be corrected to evaluate sustained deviation rate over the defined time window rather than triggering on instantaneous voltage magnitude, consistent with the operational definition of drift as a gradual and persistent condition; additionally, strict floating-point boundary comparison should be applied across all sources to prevent classification inconsistencies at threshold edges, particularly for borderline dropout readings near the warning thresholds of the Grid and Inverter sources. Beyond these technical refinements, subsequent studies should extend the monitoring duration across multiple weeks or months to capture seasonal variations in solar generation, a wider range of utility supply behaviors, and more diverse environmental and load conditions to support more statistically robust performance evaluation, while future research should explore the integration or comparative evaluation of machine learning and deep learning methods alongside the rule-based approach to assess whether adaptive detection models can improve recall performance, particularly for anomaly types exhibiting borderline or gradual threshold violations such as those observed in grid undervoltage conditions. Finally, the system should be deployed and evaluated in other hybrid power configurations, including setups incorporating wind energy, lithium-based battery storage, different inverter technologies, or multiple utility feeders, to validate its generalizability and practical scalability beyond the specific hybrid system evaluated in this study.

## Slide 57
THANK YOU!
DESIGN AND DEVELOPMENT OF EQUILOCK – AN INNOVATIVE AUTOMATED OFFICE EQUIPMENT VAULT WITH KIOSK INTERFACE FOR COLLEGE OF ENGINEERING
CAMACHO, DE CASTRO, LLARENA, TENORIO

## Slide 58
DESIGN AND DEVELOPMENT OF EQUILOCK – AN INNOVATIVE AUTOMATED OFFICE EQUIPMENT VAULT WITH KIOSK INTERFACE FOR COLLEGE OF ENGINEERING
CAMACHO, DE CASTRO, LLARENA, TENORIO

## Slide 59
DESIGN AND DEVELOPMENT OF EQUILOCK – AN INNOVATIVE AUTOMATED OFFICE EQUIPMENT VAULT WITH KIOSK INTERFACE FOR COLLEGE OF ENGINEERING
CAMACHO, DE CASTRO, LLARENA, TENORIO

## Slide 60
DESIGN AND DEVELOPMENT OF EQUILOCK – AN INNOVATIVE AUTOMATED OFFICE EQUIPMENT VAULT WITH KIOSK INTERFACE FOR COLLEGE OF ENGINEERING
CAMACHO, DE CASTRO, LLARENA, TENORIO

## Slide 61
DESIGN AND DEVELOPMENT OF EQUILOCK – AN INNOVATIVE AUTOMATED OFFICE EQUIPMENT VAULT WITH KIOSK INTERFACE FOR COLLEGE OF ENGINEERING
CAMACHO, DE CASTRO, LLARENA, TENORIO

## Slide 62
DESIGN AND DEVELOPMENT OF EQUILOCK – AN INNOVATIVE AUTOMATED OFFICE EQUIPMENT VAULT WITH KIOSK INTERFACE FOR COLLEGE OF ENGINEERING
CAMACHO, DE CASTRO, LLARENA, TENORIO

## Slide 63
Thesis Defended!
DEVELOPMENT AND PERFORMANCE EVALUATION OF A REAL-TIME ANOMALY DETECTION SYSTEM FOR HYBRID POWER OPERATION USING RULE-BASED SIGNAL ANALYSIS
ANDES, BUENAVENTURA, CALIMUTAN, CORDONATO, MANGUIAT, OCLARINO, OROZCO, RAZON